## Io Names - Aug 10
Name | Io Type | Display Value | UoM | Constant | Offset | Decimal Places | Generate Alerts | Alert time | low | high | log values type | log param 1 | log time frame | datalogger
`Store`
Store Sqft | 1 | 1 | SqFt | 1 | 0 | 0 | 0 |  |  |  | 0 |  | 0 | 0
Store $/kWh | 1 | 0.12 | $/kWh | 1 | 0 | 2 | 0 |  |  |  | 1 |  | 2 years | 0
Store Outside Temp | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  | 4 |  | 2 years | 1
Store Outside Humidity | 1 | 1 | % | 1 | 0 | 2 | 0 |  |  |  | 4 |  | 2 years | 1
Store Temp | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  | 4 |  | 2 years | 1
Store Humidity | 1 | 1 | % | 1 | 0 | 2 | 0 |  |  |  | 4 |  | 2 years | 1
Store Anti sweat Dew Point | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  | 2 | 1 | 2 years | 1
Performance Total Cost Sum Predicted | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  | 0 |  |  | 0
Performance Total Cost Sum Actual | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  | 4 |  | 2 years | 0
Performance Total kW Sum Predicted | 1 | 1 | kW | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 0
Performance Total kW Sum Actual | 1 | 1 | kW | 1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 0
Energy SEI Avg | 1 | 1 | % | 1 | 0 | 1 | 0 |  |  |  | 2 | 2 | 2 years | 0
Energy COP Avg | 1 | 1 | % | 1 | 0 | 1 | 0 |  |  |  | 2 | 2 | 2 years | 0
Energy Cost/SqFt | 1 | 1 | $/SqFt | 1 | 0 | 2 | 0 |  |  |  | 2 | 2 | 2 years | 0
Energy KBTU/kW Capacity | 1 | 1 | KBTU/kW | 1 | 0 | 2 | 0 |  |  |  | 2 | 2 | 2 years | 0
Energy MBTU/hour Cost | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  | 2 | 2 | 2 years | 0
Op Cost Total Current Day | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  | 1 |  | 2 years | 0
Op Cost Total Current Month | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  | 1 |  | 2 years | 0
Op Cost Total Current Year | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  | 1 |  | 2 years | 0
Op Cost Total Previous Day | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  | 1 |  | 2 years | 0
Op Cost Total Previous Month | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  | 1 |  | 2 years | 0
Op Cost Total Previous Year | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  | 1 |  | 2 years | 0
Op kWh Total Current Day | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 0
Op kWh Total Current Month | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 0
Op kWh Total Current Year | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 0
Op kWh Total Previous Day | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 0
Op kWh Total Previous Month | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 0
Op kWh Total Previous Year | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 0
Glycol Pump Station Status | 0 | 1 |  | 1 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0
Glycol Chiller Status | 0 | 1 |  | 1 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0
Glycol Pump Skid Amp Avg | 1 | 1 | A | 0.1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 1
Glycol Pump Skid kVA System | 1 | 1 | kVA | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
Glycol Pump Skid kVAR System | 1 | 1 | kVAR | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
Glycol Pump Skid kW Actual | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 1
Glycol Pump Skid kW Avg Demand | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
Glycol Pump Skid kW Predicted | 1 | 1 | kW | 1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 1
Glycol Pump Skid kW Peak Demand | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
Glycol Pump Skid kWh Actual | 1 | 1 | kWh | 0.1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 1
Glycol Pump Skid kWh DayStart | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 0
Glycol Pump Skid kWh DayCount | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 0
Glycol Pump Skid kWh MonthStart | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 0
Glycol Pump Skid kWh MonthCount | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 0
Glycol Pump Skid kWh YearStart | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 0
Glycol Pump Skid kWh YearCount | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 0
Glycol Pump Skid PF | 1 | 1 | PF | 0.01 | 0 | 2 | 0 |  |  |  | 5 | 1 | 2 years | 1
Glycol Pump Skid Volts Line to Line Avg | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
`Rack`
Cond Accumulated Subcool Alarm `%rackname` | 0 | 1 |  | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 |  | 2 years | 0
Cond Split Active `%rackname` | 0 | 1 |  | 1 | 0 | 0 | 0 |  |  |  | 1 |  | 2 years | 1
Cond VFD Active `%rackname` | 0 | 1 |  | 1 | 0 | 0 | 0 |  |  |  | 1 |  | 2 years | 1
Cond VFD Fault `%rackname` | 0 | 0 |  | 1 | 0 | 0 | 0 |  |  |  | 1 |  | 2 years | 1
Cond VFD Value `%rackname` | 1 | 1 | % | 1 | 0 | 1 | 0 |  |  |  | 2 | 2 | 2 years | 1
Cond Amp Avg `%rackname` | 1 | 1 | A | 0.1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 1
Cond kVA System `%rackname` | 1 | 1 | kVA | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
Cond kVAR System `%rackname` | 1 | 1 | kVAR | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
Cond kW Actual `%rackname` | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 1
Cond kW Avg Demand `%rackname` | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
Cond kW Peak Demand `%rackname` | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
Cond kW Predicted `%rackname` | 1 | 1 | kW | 1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 1
Cond kWh Actual `%rackname` | 1 | 1 | kWh | 0.1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 1
Cond kWh DayStart `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 0
Cond kWh DayCount `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 1
Cond kWh MonthStart `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 0
Cond kWh MonthCount `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 0
Cond kWh YearStart `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 0
Cond kWh YearCount `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 0
Cond Total Subcooling `%rackname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  | 4 |  | 2 years | 0
Cond Ambient Subcooling `%rackname` | 1 | 1 | F | 1 | 0 | 2 | 1 | 600 | -15 | 10 | 4 |  | 2 years | 1
Cond Subcooling Actual `%rackname` | 1 | 1 | F | 1.8 | 0 | 2 | 1 | 600 | 0.5 | 85 | 2 | 2 | 2 years | 1
Cond Subcooling Setpoint `%rackname` | 1 | 1 | F | 1.8 | 0 | 2 | 0 |  |  |  | 1 |  | 2 years | 1
Cond Outlet Pressure `%rackname` | 1 | 1 | Psig | 0.145 | 0 | 1 | 0 |  |  |  | 2 | 5 | 2 years | 1
Cond Outlet Air Temperature `%rackname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  | 2 | 5 | 2 years | 1
Cond Inlet Air Temperature `%rackname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  | 2 | 5 | 2 years | 1
Cond Downleg Temp `%rackname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  | 2 | 2 | 2 years | 1
Cond Air TD `%rackname` | 1 | 1 | F | 1 | 0 | 2 | 1 | 600 | -8 | 12 | 4 |  | 2 years | 0
Cond PF `%rackname` | 1 | 1 | PF | 0.01 | 0 | 2 | 0 |  |  |  | 5 | 1 | 90 days | 1
Cond Setpoint `%rackname` | 1 | 1 | Psig | 0.145 | 0 | 1 | 0 |  |  |  | 1 |  |  | 1
Cond Saturation `%rackname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  | 2 | 5 | 2 years | 1
Cond Volts L1 to L2 `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  | 2 | 5 | 2 years | 1
Cond Volts L1 to L3 `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  | 2 | 5 | 2 years | 1
Cond Volts L2 to L3 `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  | 2 | 5 | 2 years | 1
Cond Volts Line to Line Avg `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
Cond Volts Line to Neutral Avg `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
Cond Rack Fault `%rackname` | 1 | 1 |  | 1 | 0 | 0 | 0 |  |  |  | 1 |  | 2 years | 0
Comp Rack Fault `%rackname` | 1 | 1 |  | 1 | 0 | 0 | 0 |  |  |  | 1 |  | 2 years | 0
Comp VFD Active `%rackname` | 0 | 1 |  | 1 | 0 | 0 | 0 |  |  |  | 1 |  | 2 years | 1
Comp VFD Fault `%rackname` | 0 | 0 |  | 1 | 0 | 0 | 0 |  |  |  | 1 |  | 2 years | 1
Comp VFD Value `%rackname` | 1 | 1 | % | 1 | 0 | 1 | 0 |  |  |  | 2 | 2 | 2 years | 1
Discharge Pressure Actual `%rackname` | 1 | 1 | Psig | 0.145 | 0 | 1 | 0 |  |  |  | 2 | 3 | 2 years | 1
Discharge Tmp `%rackname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  | 2 | 3 | 2 years | 1
Op Cost Sum Current Day `%rackname` | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  | 2 | 5 | 2 years | 0
Op Cost Sum Current Month `%rackname` | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  | 2 | 5 | 2 years | 0
Op Cost Sum Current Year `%rackname` | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  | 2 | 5 | 2 years | 0
Op Cost Previous Day `%rackname` | 1 | 125 | $ | 1 | 0 | 2 | 0 |  |  |  | 2 | 5 | 2 years | 0
Op Cost Previous Month `%rackname` | 1 | 3750 | $ | 1 | 0 | 2 | 0 |  |  |  | 2 | 5 | 2 years | 0
Op Cost Previous Year `%rackname` | 1 | 42950 | $ | 1 | 0 | 2 | 0 |  |  |  | 2 | 5 | 2 years | 0
Op kWh Current Day `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 2 | 5 | 2 years | 0
Op kWh Current Month `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 2 | 5 | 2 years | 0
Op kWh Current Year `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 2 | 5 | 2 years | 0
Op kWh Counter Current Day `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 2 | 5 | 2 years | 0
Op kWh Counter Current Month `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 2 | 5 | 2 years | 0
Op kWh Counter Current Year `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 2 | 5 | 2 years | 0
Op kWh Previous Day `%rackname` | 1 | 1000 | kWh | 1 | 0 | 1 | 0 |  |  |  | 1 |  | 2 years | 0
Op kWh Previous Month `%rackname` | 1 | 30000 | kWh | 1 | 0 | 1 | 0 |  |  |  | 1 |  | 2 years | 0
Op kWh Previous Year `%rackname` | 1 | 360000 | kWh | 1 | 0 | 1 | 0 |  |  |  | 1 |  | 2 years | 0
Performance Cost Sum Predicted `%rackname` | 1 | 1 | $ | 1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 0
Performance Cost Sum Actual `%rackname` | 1 | 1 | $ | 1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 0
Performance kW Sum Predicted `%rackname` | 1 | 1 | kW | 1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 0
Performance kW Sum Actual `%rackname` | 1 | 1 | kW | 1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 0
Amp Avg `%rackname` | 1 | 1 | A | 0.1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 1
kVA System `%rackname` | 1 | 1 | kVA | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
kVAR System `%rackname` | 1 | 1 | kVAR | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
kW Actual `%rackname` | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 1
kW Avg Demand `%rackname` | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
kW Predicted `%rackname` | 1 | 1 | kW | 1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 1
kW Peak Demand `%rackname` | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 90 days | 1
kWh Actual `%rackname` | 1 | 1 | kWh | 0.1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 1
PF `%rackname` | 1 | 1 | PF | 0.01 | 0 | 2 | 0 |  |  |  | 5 | 1 | 2 years | 1
Rack SEI `%rackname` | 1 | 1 | % | 1 | 0 | 1 | 0 |  |  |  | 2 | 2 | 2 years | 0
COP `%rackname` | 1 | 1 | % | 1 | 0 | 1 | 0 |  |  |  | 2 | 2 | 2 years | 0
Volts L1 to L2 `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  | 2 | 5 | 2 years | 1
Volts L1 to L3 `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  | 2 | 5 | 2 years | 1
Volts L2 to L3 `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  | 2 | 5 | 2 years | 1
Volts Line to Line Avg `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
Volts Line to Neutral Avg `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
Refrigerant Type `%rackname` | 1 | 507 |  | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 0
Refrigerant Level `%rackname` | 1 | 1 | % (Level) | 1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 1
`Condenser`
Cond Fan Amps `%rackname` `%fannum` | 1 | 0.1 | A | 1 | 0 | 1 | 0 |  |  |  | 2 | 5 | 2 years | 1
Cond Fan Status `%rackname` `%fannum` | 1 | 1 |  | 1 | 0 | 0 | 0 |  |  |  | 1 |  | 2 years | 1
Cond Fan RUN `%rackname` `%fannum` | 0 | 1 |  | 1 | 0 | 0 | 0 |  |  |  | 1 |  | 2 years | 1
`Suction Group`
Suction Temp `%rackname` `%sgname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  | 2 | 5 | 2 years | 1
Suction Saturation `%rackname` `%sgname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  | 2 | 5 | 2 years | 1
Suction Pressure Float Failure `%rackname` `%sgname` | 0 | 0 |  | 1 | 0 | 0 | 1 | 300 | 1 | 1 | 1 |  | 2 years | 0
Suction Pressure Accumulated `%rackname` `%sgname` | 0 | 1 |  | 1 | 0 | 0 | 1 | 300 | 1 | 1 | 1 |  | 2 years | 0
Suction Pressure Actual `%rackname` `%sgname` | 1 | 1 | Psig | 0.145 | 0 | 1 | 0 |  |  |  | 2 | 2 | 2 years | 1
Suction Pressure Setpoint `%rackname` `%sgname` | 1 | 1 | Psig | 0.145 | 0 | 1 | 1 | 300 | 0 | 150 | 1 |  | 2 years | 1
Suction Pressure Design Setpoint `%rackname` `%sgname` | 1 | 11.6 | Psig | 1 | 0 | 1 | 0 | [5 empty] | 2 years | 0
Suction Superheat `%rackname` `%sgname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  | 2 | 5 | 2 years | 1
`System`
System Capacity `%rackname` `%sgname` `%sysname` | 1 | 1 | BTU/H | 1 | 0 | 1 | 0 |  |  |  | 1 |  | 2 years | 1
System EEPR `%rackname` `%sgname` `%sysname` | 1 | 1 | % | 1 | 0 | 1 | 0 |  |  |  | 2 | 5 | 2 years | 1
System EEPR Predicted `%rackname` `%sgname` `%sysname` | 1 | 1 | % | 1 | 0 | 1 | 0 |  |  |  | 2 | 5 | 2 years | 0
System kW `%rackname` `%sgname` `%sysname` | 1 | 1 | kW | 1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 1
System Setpoint `%rackname` `%sgname` `%sysname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  | 1 |  | 2 years | 1
System Temp `%rackname` `%sgname` `%sysname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  | 2 | 3 | 2 years | 1
System Defrost Status `%rackname` `%sgname` `%sysname` | 0 | 0 |  | 1 | 0 | 0 | 0 |  |  |  | 1 |  | 2 years | 1
System Defrost Temp `%rackname` `%sgname` `%sysname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  | 2 | 3 | 2 years | 1
System Status `%rackname` `%sgname` `%sysname` | 0 | 1 |  | 1 | 0 | 0 | 1 | 5 | 1 | 1 | 1 |  | 2 years | 1
`Compressor`
Comp Amps `%rackname` `%sgname` `%compname` | 1 | 1 | A | 0.1 | 0 | 1 | 1 | 240 | 0 | 50 | 5 | 1 | 180 days | 1
Comp Discharge Temp `%rackname` `%sgname` `%compname` | 1 | 1 | F | 1.8 | -32 | 2 | 1 | 180 | -30 | 225 | 5 | 1 | 180 days | 1
Comp Status `%rackname` `%sgname` `%compname` | 1 | 1 |  | 1 | 0 | 0 | 0 |  |  |  | 5 | 1 | 180 days | 1
Comp SLA `%rackname` `%sgname` `%compname` | 0 | 0 |  | 1 | 0 | 0 | 0 |  |  |  | 1 |  | 2 years | 1
Comp RUN `%rackname` `%sgname` `%compname` | 0 | 1 |  | 1 | 0 | 0 | 0 |  |  |  | 1 |  | 2 years | 1
Comp kW `%rackname` `%sgname` `%compname` | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 180 days | 1
`Glycol`
Glycol Status `%glycolname` | 1 | 1 |  | 1 | 0 | 0 | 0 |  |  |  | 5 | 1 | 180 days
Glycol System Capacity `%glycolname` | 1 | 1 | BTU/H | 1 | 0 | 1 | 0 |  |  |  | 1 |  | 2 years | 1
Glycol System Temp `%glycolname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  | 2 | 5 | 2 years | 1
Glycol System Setpoint `%glycolname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  | 1 |  |  | 1
`FanPanel`
Fan Panel Amp Avg `%fanpanelnum` | 1 | 1 | A | 0.1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 1
Fan Panel kVA System `%fanpanelnum` | 1 | 1 | kVA | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
Fan Panel kVAR System `%fanpanelnum` | 1 | 1 | kVAR | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
Fan Panel kW Actual `%fanpanelnum` | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 1
Fan Panel kW Avg Demand `%fanpanelnum` | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
Fan Panel kW Predicted `%fanpanelnum` | 1 | 1 | kW | 1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 1
Fan Panel kW Peak Demand `%fanpanelnum` | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
Fan Panel kWh Actual `%fanpanelnum` | 1 | 1 | kWh | 0.1 | 0 | 1 | 0 |  |  |  | 4 |  | 2 years | 1
Fan Panel kWh DayStart `%fanpanelnum` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 0
Fan Panel kWh DayCount `%fanpanelnum` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 0
Fan Panel kWh MonthStart `%fanpanelnum` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 0
Fan Panel kWh MonthCount `%fanpanelnum` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 0
Fan Panel kWh YearStart `%fanpanelnum` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 0
Fan Panel kWh YearCount `%fanpanelnum` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  | 0 |  |  | 0
Fan Panel PF `%fanpanelnum` | 1 | 1 | PF | 0.01 | 0 | 2 | 0 |  |  |  | 5 | 1 | 2 years | 1
Fan Panel Volts Line to Line Avg `%fanpanelnum` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1
Fan Panel Volts Line to Line Avg `%fanpanelnum` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  | 5 | 1 | 2 years | 1