## Sheet1
Name | IO Type | Display Value | UoM | Constant | Offset | Decimal Places | Generate Alerts | Alert Templates | Alert Time Frame | Low Alert | High Alert | Log Values | Log Param | Log Time Period
`Store`
Store Sqft | 1 | 1 | SqFt | 1 | 0 | 0 | 0 |  |  |  |  | 0
Store $/kWh | 3 | 0.12 | $/kWh | 1 | 0 | 2 | 0 |  |  |  |  | 1 |  | 2 years
Store Outside Temp | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  |  | 2 | 1 | 2 years
Store Outside Humidity | 1 | 1 | % | 1 | 0 | 2 | 0 |  |  |  |  | 2 | 1 | 2 years
Store Temp | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  |  | 2 | 1 | 2 years
Store Humidity | 1 | 1 | % | 1 | 0 | 2 | 0 |  |  |  |  | 2 | 1 | 2 years
Store Anti sweat Dew Point | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  |  | 2 | 1 | 2 years
Performance Total Cost Sum Predicted | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  |  | 0
Performance Total Cost Sum Actual | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  |  | 4 |  | 2 years
Performance Total kW Sum Predicted | 1 | 1 | kW | 1 | 0 | 1 | 0 |  |  |  |  | 0
Performance Total kW Sum Actual | 1 | 1 | kW | 1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
Energy SEI Avg | 1 | 1 | % | 1 | 0 | 1 | 0 |  |  |  |  | 2 | 2 | 2 years
Energy COP Avg | 1 | 1 | % | 1 | 0 | 1 | 0 |  |  |  |  | 2 | 2 | 2 years
Energy Cost/SqFt | 1 | 1 | $/SqFt | 1 | 0 | 2 | 0 |  |  |  |  | 2 | 2 | 2 years
Energy KBTU/kW Capacity | 1 | 1 | KBTU/kW | 1 | 0 | 2 | 0 |  |  |  |  | 2 | 2 | 2 years
Energy MBTU/hour Cost | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  |  | 2 | 2 | 2 years
Op Cost Total Current Day | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  |  | 0
Op Cost Total Current Month | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  |  | 0
Op Cost Total Current Year | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  |  | 0
Op Cost Total Previous Day | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  |  | 1 |  | 2 years
Op Cost Total Previous Month | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  |  | 1 |  | 2 years
Op Cost Total Previous Year | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  |  | 1 |  | 2 years
Op kWh Total Current Day | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
Op kWh Total Current Month | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
Op kWh Total Current Year | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
Op kWh Total Previous Day | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
Op kWh Total Previous Month | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
Op kWh Total Previous Year | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
`Rack`
Amp Avg `%rackname` | 1 | 1 | A | 0.1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
Cond Amp Avg `%rackname` | 1 | 1 | A | 0.1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
Cond kVA System `%rackname` | 1 | 1 | kVA | 0.1 | 0 | 1 | 0 |  |  |  |  | 5 | 1 | 90 days
Cond kVAR System `%rackname` | 1 | 1 | kVAR | 0.1 | 0 | 1 | 0 |  |  |  |  | 5 | 1 | 90 days
Cond kW Actual `%rackname` | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
Cond kW Avg Demand `%rackname` | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  |  | 5 | 1 | 90 days
Cond kW Peak Demand `%rackname` | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  |  | 5 | 1 | 90 days
Cond kW Predicted `%rackname` | 1 | 1 | kW | 1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
Cond kWh Actual `%rackname` | 1 | 1 | kWh | 0.1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
Cond kWh DayStart `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  |  | 0
Cond kWh DayCount `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  |  | 0
Cond Outlet Subcooling `%rackname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  |  | 0
Cond Outlet Pressure `%rackname` | 1 | 1 | Psig | 0.145 | 1 | 1 | 0 |  |  |  |  | 0
Cond Outlet Temperature `%rackname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  |  | 0
Cond PF `%rackname` | 1 | 1 | PF | 0.01 | 0 | 2 | 0 |  |  |  |  | 5 | 1 | 90 days
Cond Setpoint `%rackname` | 1 | 1 | Psig | 0.145 | 0 | 1 | 0 |  |  |  |  | 0
Cond Saturation `%rackname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  |  | 0
Cond Volts L1 to L2 `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  |  | 0
Cond Volts L1 to L3 `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  |  | 0
Cond Volts L2 to L3 `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  |  | 0
Cond Volts Line to Line Avg `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  |  | 5 | 1 | 90 days
Cond Volts Line to Neutral Avg `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  |  | 5 | 1 | 90 days
Comp Rack Fault `%rackname` | 1 | 1 |  | 1 | 0 | 0 | 0 |  |  |  |  | 0
Cond Rack Fault `%rackname` | 1 | 1 |  | 1 | 0 | 0 | 0 |  |  |  |  | 0
Discharge Pressure Actual `%rackname` | 1 | 1 | Psig | 0.145 | 0 | 1 | 0 |  |  |  |  | 0
Discharge Tmp `%rackname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  |  | 0
kVA System `%rackname` | 1 | 1 | kVA | 0.1 | 0 | 1 | 0 |  |  |  |  | 5 | 1 | 90 days
kVAR System `%rackname` | 1 | 1 | kVAR | 0.1 | 0 | 1 | 0 |  |  |  |  | 5 | 1 | 90 days
kW Actual `%rackname` | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
kW Avg Demand `%rackname` | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  |  | 5 | 1 | 90 days
kW Predicted `%rackname` | 1 | 1 | kW | 1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
kW Peak Demand `%rackname` | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  |  | 5 | 1 | 90 days
kWh Actual `%rackname` | 1 | 1 | kWh | 0.1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
Liquid Total Subcooling `%rackname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  |  | 0
Liquid Subcooling `%rackname` | 1 | 1 | F | 1.8 | -32 | 2 | 1 | 11 | 300 | 2 | 115 | 0
Op Cost Current Day `%rackname` | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  |  | 0
Op Cost Current Month `%rackname` | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  |  | 0
Op Cost Current Year `%rackname` | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  |  | 0
Op Cost Sum Current Day `%rackname` | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  |  | 0
Op Cost Sum Current Month `%rackname` | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  |  | 0
Op Cost Sum Current Year `%rackname` | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  |  | 0
Op Cost Previous Day `%rackname` | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  |  | 0
Op Cost Previous Month `%rackname` | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  |  | 0
Op Cost Previous Year `%rackname` | 1 | 1 | $ | 1 | 0 | 2 | 0 |  |  |  |  | 0
Op kWh Current Day `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  |  | 0
Op kWh Current Month `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  |  | 0
Op kWh Current Year `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  |  | 0
Op kWh Counter Current Day `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  |  | 0
Op kWh Counter Current Month `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  |  | 0
Op kWh Counter Current Year `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  |  | 0
Op kWh Previous Day `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  |  | 1 |  | 2 years
Op kWh Previous Month `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  |  | 1 |  | 2 years
Op kWh Previous Year `%rackname` | 1 | 1 | kWh | 1 | 0 | 1 | 0 |  |  |  |  | 1 |  | 2 years
Performance Cost Sum Predicted `%rackname` | 1 | 1 | $ | 1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
Performance Cost Sum Actual `%rackname` | 1 | 1 | $ | 1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
Performance kW Sum Predicted `%rackname` | 1 | 1 | kW | 1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
Performance kW Sum Actual `%rackname` | 1 | 1 | kW | 1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
PF `%rackname` | 1 | 1 | PF | 0.01 | 0 | 2 | 0 |  |  |  |  | 5 | 1 | 90 days
SEI `%rackname` | 1 | 1 | % | 1 | 0 | 1 | 0 |  |  |  |  | 2 | 2 | 2 years
COP `%rackname` | 1 | 1 | % | 1 | 0 | 1 | 0 |  |  |  |  | 2 | 2 | 2 years
Volts L1 to L2 `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  |  | 0
Volts L1 to L3 `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  |  | 0
Volts L2 to L3 `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  |  | 0
Volts Line to Line Avg `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  |  | 5 | 1 | 90 days
Volts Line to Neutral Avg `%rackname` | 1 | 1 | V | 0.1 | 0 | 1 | 0 |  |  |  |  | 5 | 1 | 90 days
Refrigerant Type `%rackname` | 1 | 1 |  | 1 | 0 | 1 | 0 |  |  |  |  | 0
`Condenser`
Cond Fan Amps `%rackname` `%fannum` | 1 | 1 | A | 1 | 0 | 1 | 0 |  |  |  |  | 0
Cond Fan Status `%rackname` `%fannum` | 1 | 1 |  | 1 | 0 | 0 | 0 |  |  |  |  | 0
Cond Fan RUN `%rackname` `%fannum` | 0 | 1 |  | 1 | 0 | 0 | 0 |  |  |  |  | 0
`Suction Group`
Suction Temp `%rackname` `%sgname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  |  | 0
Suction Pressure Actual `%rackname` `%sgname` | 1 | 1 | Psig | 0.145 | 0 | 1 | 0 |  |  |  |  | 0
Suction Pressure Effective Setpoint `%rackname` `%sgname` | 1 | 1 | Psig | 0.145 | 0 | 1 | 0 |  |  |  |  | 0
Suction Pressure Setpoint `%rackname` `%sgname` | 1 | 1 | Psig | 0.145 | 0 | 1 | 0 |  |  |  |  | 0
Suction Pressure Design Setpoint `%rackname` `%sgname` | 1 | 1 | Psig | 1 | 0 | 1 | 0 |  |  |  |  | 0
Suction Saturation `%rackname` `%sgname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  |  | 0
Suction Superheat `%rackname` `%sgname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  |  | 0
`System`
System Capacity `%rackname` `%sgname` `%sysname` | 1 | 1 | BTU/H | 1 | 0 | 1 | 0 |  |  |  |  | 0
System EEPR `%rackname` `%sgname` `%sysname` | 1 | 1 | % | 1 | 0 | 1 | 0 |  |  |  |  | 0
System EEPR Predicted `%rackname` `%sgname` `%sysname` | 1 | 1 | % | 1 | 0 | 1 | 0 |  |  |  |  | 0
System kW `%rackname` `%sgname` `%sysname` | 1 | 1 | kW | 1 | 0 | 1 | 0 |  |  |  |  | 4 |  | 2 years
System Setpoint `%rackname` `%sgname` `%sysname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  |  | 1 |  | 2 years
System Temp `%rackname` `%sgname` `%sysname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  |  | 0
System Status `%rackname` `%sgname` `%sysname` | 1 | 1 |  | 1 | 0 | 0 | 0 |  |  |  |  | 0
`Compressor`
Comp Amps `%rackname` `%sgname` `%compname` | 1 | 1 | A | 0.1 | 0 | 1 | 0 |  |  |  |  | 5 | 1 | 180 days
Comp Amp Limit `%rackname` `%sgname` `%compname` | 1 | 1 | A | 1 | 0 | 1 | 0 |  |  |  |  | 0
Comp Discharge Temp `%rackname` `%sgname` `%compname` | 1 | 1 | F | 1.8 | -32 | 2 | 1 | 5 | 180 | -30 | 225 | 5 | 1 | 180 days
Comp Discharge Limit `%rackname` `%sgname` `%compname` | 1 | 1 | F | 1.8 | -32 | 2 | 0 |  |  |  |  | 0
Comp Status `%rackname` `%sgname` `%compname` | 1 | 1 |  | 1 | 0 | 0 | 0 |  |  |  |  | 5 | 1 | 180 days
Comp SLA `%rackname` `%sgname` `%compname` | 0 | 1 |  | 1 | 0 | 0 | 0 |  |  |  |  | 0
Comp RUN `%rackname` `%sgname` `%compname` | 0 | 1 |  | 1 | 0 | 0 | 0 |  |  |  |  | 0
Comp kW `%rackname` `%sgname` `%compname` | 1 | 1 | kW | 0.1 | 0 | 1 | 0 |  |  |  |  | 5 | 1 | 180 days