## taskSheet
description of task | task_manager_name | task_manager_task_id | task_manager_inputs | task_manager_outputs | task_manager_crontab_line | task_manager_pass_inputs_as_io_id | EachRack
Converts kW to $ based on the $/kWh value | Actual_Costs_kW All Racks | 24 | Store $/kWh,Performance kW Sum Predicted `%rackname`,Performance kW Sum Actual `%rackname`,Performance Total kW Sum Predicted | Performance Cost Sum Predicted `%rackname`,Performance Cost Sum Actual `%rackname`,Performance Total Cost Sum Predicted | * * * * * | 0 | 1
Average all Rack SEI values into a total variable | Avg_Items All Racks | 30 | Rack SEI `%rackname` | Energy SEI Avg | * * * * * | 0 | 1
Average all Rack COP values into a total variable | Avg_Items All Racks | 30 | COP `%rackname` | Energy COP Avg | * * * * * | 0 | 1
Find the compressor status for the individual compressors on the Rack | CompStatus `%rackname` | 34 | Comp Amps `%rackname` `%sgname` `%compname`,Comp SLA `%rackname` `%sgname` `%compname`,Comp Discharge Temp `%rackname` `%sgname` `%compname` | Comp Status `%rackname` `%sgname` `%compname` | * * * * * | 0 | 2
Find the condenser fan status for the individual condensers on the Rack | CondFanStatus `%rackname` | 40 | Cond Fan Amps `%rackname` `%fannum`,Cond Fan RUN `%rackname` `%fannum`,Cond Fan Status `%rackname` `%fannum` | Cond Fan Status `%rackname` `%fannum` | * * * * * | 0 | 2
Find the predicted value for the IO input | DbFindPredicted All Racks | 38 | Store Outside Temp,Cond kW Avg Demand `%rackname`,kW Avg Demand `%rackname` | Cond kW Predicted `%rackname`,kW Predicted `%rackname` | 2-59/3 * * * * | 1 | 1
Save the demand value | DbSavePredicted All Racks | 37 | Store Outside Temp,Cond kW Avg Demand `%rackname`,kW Avg Demand `%rackname` | Blank | */15 * * * * | 1 | 1
Check all compressor status' for the LED on the main page | FaultCompressors `%rackname` | 41 | Comp Status `%rackname` `%sgname` `%compname` | Comp Rack Fault `%rackname` | * * * * * | 0 | 2
Check all condensers status' for the LED on the main page | FaultCondensers `%rackname` | 42 | Cond Fan Status `%rackname` `%sgname` `%compname` | Cond Rack Fault `%rackname` | * * * * * | 0 | 2
Calculates the running kWh total for condensers on a Rack | kWh_Cond_Sum All Racks | 26 | Cond kWh Actual `%rackname`,Cond kWh DayStart `%rackname` | Cond kWh DayCount `%rackname` | * * * * * | 0 | 1
Calculates the running kWh total for the Rack | kWh_Sum All Racks | 17 | kWh Actual `%rackname`,Op kWh Current Day `%rackname`,Op kWh Current Month `%rackname`,Op kWh Current Year `%rackname`,Cond kWh DayCount `%rackname` | Op kWh Counter Current Day `%rackname`,Op kWh Counter Current Month `%rackname`,Op kWh Counter Current Year `%rackname` | * * * * * | 0 | 1
Convert OP Cost kWh to OP Cost Sum | OperatingCosts All Racks | 21 | Store $/kWh,Op kWh Counter Current Day `%rackname`,Op kWh Counter Current Month `%rackname`,Op kWh Counter Current Year `%rackname` | Op Cost Sum Current Day `%rackname`,Op Cost Sum Current Month `%rackname`,Op Cost Sum Current Year `%rackname` | 3-59/1 * * * * | 0 | 1
Adds the condenser and the rack predicted kw values to the Performance kW Sum variable | PredictedRackSumkW All Racks | 39 | kW Predicted `%rackname`,Cond kW Predicted `%rackname` | Performance kW Sum Predicted `%rackname` | * * * * * | 0 | 1
Calculate SEI for an individual rack | SEI_ALL_VALUES `%rackname` | 31 | Refrigerant Type `%rackname`,Store Outside Temp,Cond Outlet Pressure `%rackname`,Cond Outlet Temperature `%rackname`,Discharge Pressure Actual `%rackname`,Discharge Tmp `%rackname`,Suction Temp `%rackname` `%sgname`,Suction Pressure Actual `%rackname` `%sgname`,Rack SEI `%rackname` | COP `%rackname`,Rack SEI `%rackname`,Cond Total Subcooling `%rackname`,Suction Superheat `%rackname` `%sgname` | * * * * * | 0 | 1
Reset a time period for the kWh. DAY PERIOD | kWh Reset Day All Racks | 19 | Op kWh Counter Current Day `%rackname`,kWh Actual `%rackname` | Op kWh Previous Day `%rackname`,Op kWh Current Day `%rackname`,Op kWh Counter Current Day `%rackname` | 1 0 * * * | 0 | 1
Reset a time period for the kWh. MONTH PERIOD | kWh Reset Month All Racks | 19 | Op kWh Counter Current Month `%rackname`,kWh Actual `%rackname` | Op kWh Previous Month `%rackname`,Op kWh Current Month `%rackname`,Op kWh Counter Current Month `%rackname` | 1 0 1 * * | 0 | 1
Reset a time period for the kWh. YEAR PERIOD | kWh Reset Year All Racks | 19 | Op kWh Counter Current Year `%rackname`,kWh Actual `%rackname` | Op kWh Previous Year `%rackname`,Op kWh Current Year `%rackname`,Op kWh Counter Current Year `%rackname` | 1 0 1 1 * | 0 | 1
Reset a time period for the Operating Cost. DAY PERIOD | OP Cost Day | 22 | Op Cost Sum Current Day `%rackname` | Op Cost Previous Day `%rackname`,Op Cost Sum Current Day `%rackname` | 2 0 * * * | 0 | 1
Reset a time period for the Operating Cost. MONTH PERIOD | OP Cost Month | 22 | Op Cost Sum Current Month `%rackname` | Op Cost Previous Month `%rackname`,Op Cost Sum Current Month `%rackname` | 2 0 1 * * | 0 | 1
Reset a time period for the Operating Cost. YEAR PERIOD | OP Cost Year | 22 | Op Cost Sum Current Year `%rackname` | Op Cost Previous Year `%rackname`,Op Cost Sum Current Year `%rackname` | 2 0 1 1 * | 0 | 1
Calculate the store costs for the financial page. | StoreCosts All Racks | 29 | Energy COP Avg,Store $/kWh,Op Cost Total Previous Month,Store Sqft | Energy KBTU/kW Capacity,Energy MBTU/hour Cost,Energy Cost/SqFt | * * * * * | 0 | 0
Reset the Cond kWh counter at 12:01am | SetCurrentkWhCondMultiple All Racks | 27 | Cond kWh Actual `%rackname` | Cond kWh DayStart `%rackname`,Cond kWh DayCount `%rackname` | 1 0 * * * | 0 | 1
Adds the item up. Performance kW Sum | Sum kW `%rackname` | 23 | kW Actual `%rackname`,Cond kW Actual `%rackname` | Performance kW Sum Actual `%rackname` | * * * * * | 0 | 0
Adds the item up. Performance Total kW Sum | Sum kW Total Actual | 23 | Performance kW Sum Actual `%rackname` | Performance Total kW Sum Actual | * * * * * | 0 | 1
Adds the item up. Performance Total kW Sum | Sum kW Total Predicted | 23 | Performance kW Sum Predicted `%rackname` | Performance Total kW Sum Predicted | * * * * * | 0 | 1
Adds the item up. Performance Total Cost | Sum Cost Total Actual | 23 | Performance Cost Sum Actual `%rackname` | Performance Total Cost Sum Actual | * * * * * | 0 | 1
Operating kWh Total Previous Day | Sum kWh Total Prev Day | 23 | Op kWh Previous Day `%rackname` | Op kWh Total Previous Day | * * * * * | 0 | 1
Operating kWh Total Previous Month | Sum kWh Total Prev Month | 23 | Op kWh Previous Month `%rackname` | Op kWh Total Previous Month | * * * * * | 0 | 1
Operating kWh Total Previous Year | Sum kWh Total Prev Year | 23 | Op kWh Previous Year `%rackname` | Op kWh Total Previous Year | * * * * * | 0 | 1
Operating kWh Total Counter Current Day | Sum kWh Total Curr Day | 23 | Op kWh Counter Current Day `%rackname` | Op kWh Total Current Day | * * * * * | 0 | 1
Operating kWh Total Counter Current Month | Sum kWh Total Curr Month | 23 | Op kWh Counter Current Month `%rackname` | Op kWh Total Current Month | * * * * * | 0 | 1
Operating kWh Total Counter Current Year | Sum kWh Total Curr Year | 23 | Op kWh Counter Current Year `%rackname` | Op kWh Total Current Year | * * * * * | 0 | 1
Operating Cost Current Day | Sum Op Cost Curr Day | 23 | Op Cost Sum Current Day `%rackname` | Op Cost Total Current Day | * * * * * | 0 | 1
Operating Cost Current Month | Sum Op Cost Curr Month | 23 | Op Cost Sum Current Month `%rackname` | Op Cost Total Current Month | * * * * * | 0 | 1
Operating Cost Current Year | Sum Op Cost Curr Year | 23 | Op Cost Sum Current Year `%rackname` | Op Cost Total Current Year | * * * * * | 0 | 1
Operating Cost Previous Day | Sum Op Cost Prev Day | 23 | Op Cost Previous Day `%rackname` | Op Cost Total Previous Day | */5 * * * * | 0 | 1
Operating Cost Previous Month | Sum Op Cost Prev Month | 23 | Op Cost Previous Month `%rackname` | Op Cost Total Previous Month | */5 * * * * | 0 | 1
Operating Cost Previous Year | Sum Op Cost Prev Year | 23 | Op Cost Previous Year `%rackname` | Op Cost Total Previous Year | */5 * * * * | 0 | 1
Finds the difference between the cond variables | Cond Temp Difference | 25 | Cond Outlet Air Temperature `%rackname`,Cond Inlet Air Temperature `%rackname` | Cond Air TD `%rackname` | * * * * * | 0 | 1
Finds the difference between the cond variables | Cond Ambient Subcooling Difference | 25 | Cond Downleg Temperature `%rackname`,Cond Inlet Air Temperature `%rackname` | Cond Ambient Subcooling `%rackname` | * * * * * | 0 | 1